## Sheet1
Number | Section | SectionDescription | Description
1 | 01 | PreliminaryReview | Quickly make an overview of all sheets spending no more than one minute per sheet to become familiar with the project
2 | 02 | Specifications | Check specs for bid items - are they coordinated with the drawings
3 | 02 | Specifications | Check specs for phasing of construction - are the phases clear
4 | 02 | Specifications | Compare architectural finish schedule to specification index - ensure all finish materials are specified
5 | 02 | Specifications | Check major items of equipment and verify that they are coordinated with contract drawings - pay particular attention to horsepower ratings and voltage requirements
6 | 02 | Specifications | Verify that items specified "as indicated" or "where indicated are in fact indicated on contract drawings
7 | 02 | Specifications | Try not to indicate thickness of materials or quantities of materials in specifications
8 | 03 | Plan Check | Verify that site plans with new underground utilities (power, telephone, water, sewer, gas, storm drainage, fuel lines, grease traps, fuel tanks) have been checked for interferences
9 | 03 | Plan Check | Verify that existing telephone poles, pole guys, street signs, drainage inlets, valve boxes, manhole castings, etc., do not interfere with new driveways, sidewalks, or other site improvements on architectural site plans
10 | 03 | Plan Check | Verify that limits of clearing, grading, sodding, grass or mulch are shown and are consistent with architectural or landscape plans
11 | 03 | Plan Check | Verify fire hydrant and street light pole locations against electrical and architectural
12 | 03 | Plan Check | Verify that profile sheets show other underground utilities and avoid conflicts
13 | 03 | Plan Check | Verify that horizontal distances between drainage structures and manholes match with respect to scaled dimensions and stated dimensions on both plan and profile sheets
14 | 03 | Plan Check | Verify that provisions have been included for adjusting valve box and manhole casting to match final or finish grade of pavement, swales, or sidewalks
15 | 03 | Plan Check | Verify that all existing and proposed grades are shown
16 | 04 | Structural | Verify column lines on structural and architectural
17 | 04 | Structural | Verify that all column locations are the same on structural and architectural
18 | 04 | Structural | Verify that perimeter slab on structural matches architectural
19 | 04 | Structural | Verify that all depressed or raised slabs are indicated
20 | 04 | Structural | Verify slab elevations against architectural
21 | 04 | Structural | Verify that all foundation piers are identified
22 | 04 | Structural | Verify roof framing plan column lines and columns against foundation plan column lines an columns
23 | 04 | Structural | Verify perimeter roof line against architectural roof plan
24 | 04 | Structural | Verify that all columns and beams are listed in column and beam schedules
25 | 04 | Structural | Verify length of all columns in column schedule
26 | 04 | Structural | Verify that all sections are properly labeled
27 | 04 | Structural | Verify all expansion joint locations against architectural
28 | 04 | Structural | Verify dimensions
29 | 04 | Structural | Verify that drawing notes do not conflict with specifications
30 | 05 | Architectural | Verify property line dimensions on site survey plan against architecture
31 | 05 | Architectural | Verify that building is located behind setback lines
32 | 05 | Architectural | Verify all concrete columns and walls against structural
33 | 05 | Architectural | Verify on site plans that existing and new work is clearly identified
34 | 05 | Architectural | Verify building elevations against floor plans - check in particular roof lines, window and door openings, and expansion joints
35 | 05 | Architectural | Verify building sections against elevations and plans - check roof lines windows, and door locations
36 | 05 | Architectural | Verify wall sections against architectural building sections and structural
37 | 05 | Architectural | Verify masonry openings for windows and doors
38 | 05 | Architectural | Verify expansion joints through building
39 | 05 | Architectural | Verify partial floor plans against small scale floor plans
40 | 05 | Architectural | Verify reflected ceiling plan against architectural floor plan to ensure no variance in rooms - check ceiling materials against finish schedule, check light fixture layout against electrical, check ceiling diffusers/registers against mechanical, check all
41 | 05 | Architectural | Verify all room finish schedule information including room numbers, names of rooms, finishes, ceiling heights - look for omissions, duplications and inconsistencies
42 | 05 | Architectural | Verify all rated walls
43 | 05 | Architectural | Verify all cabinets will fit
44 | 05 | Architectural | Verify dimensions
45 | 06 | Mechanical and Plumbing | Verify that all new electrical, gas, water, sewer, etc. lines connect to existing
46 | 06 | Mechanical and Plumbing | Verify all plumbing fixture locations against architectural - verify all plumbing fixtures against fixture schedule and/or specs
47 | 06 | Mechanical and Plumbing | Verify storm drainage system against architectural roof plan - verify that pipes are sized and all drains are connected and no not interfere with foundations - verify that wall chases are provided on architectural conceal architectural piping
48 | 06 | Mechanical and Plumbing | Verify that sanitary drain system pipes are sized and all fixtures are connected
49 | 06 | Mechanical and Plumbing | Verify HVAC floor plans against architectural
50 | 06 | Mechanical and Plumbing | Verify sprinkler heads in all rooms
51 | 06 | Mechanical and Plumbing | Verify that all sections are identical to architectural/structural
52 | 06 | Mechanical and Plumbing | Verify that adequate ceiling height exists at worst case duct intersection
53 | 06 | Mechanical and Plumbing | Verify that all structural supports required for mechanical equipment are indicated on structural drawings
54 | 06 | Mechanical and Plumbing | Verify that dampers are indicated at smoke and fire walls
55 | 06 | Mechanical and Plumbing | Verify diffusers against architectural reflected ceiling plan
56 | 06 | Mechanical and Plumbing | Verify that all roof penetrations (duct, fans, etc.) are indicated on roof plans
57 | 06 | Mechanical and Plumbing | Verify all ductwork is sized
58 | 06 | Mechanical and Plumbing | Verify all notes
59 | 06 | Mechanical and Plumbing | Verify all air conditioning units, heaters, and exhaust fans against architectural roof plans and mechanical schedules
60 | 06 | Mechanical and Plumbing | Verify that all mechanical equipment will fit in spaces allocated
61 | 07 | Electrical | Verify that all plans are identical to architectural
62 | 07 | Electrical | Verify all light fixtures against architectural reflected ceiling plan
63 | 07 | Electrical | Verify that all major pieces of equipment have electrical connections
64 | 07 | Electrical | Verify location of all panel boards and that they are indicated on the electrical riser diagram
65 | 07 | Electrical | Verify all notes
66 | 07 | Electrical | Verify that there is sufficient space for all electrical panels to fit
67 | 07 | Electrical | Verify that the electrical panels are not recessed in fire walls
68 | 07 | Electrical | Verify that electrical equipment locations are coordinated with site paving and grading
69 | 07 | Electrical | Verify equipment layout against architectural plans