## Sheet1
Number | Section | SectionDescription | Description
1 | 01 | General | Work complies with local, state, and adopted national codes; areas where no local codes exist governed by state code regulations
2 | 01 | General | All parts of system visible for inspection
3 | 01 | General | All piping wrapped or otherwise protected when passing through concrete
4 | 01 | General | Notches not made in the middle third of the joist span; notches do not exceed 1/6 the depth of the joist except at the ends, where notches may be 1/4 the depth of the joist
5 | 01 | General | Holes in joists do not exceed 1/3 the depth of the joist and are not within 2 inches of the top or bottom edges of the joist
6 | 01 | General | Holes bored through plates draftstopped with caulking or foam insulation
7 | 01 | General | Nail plates installed over studs, sole plates, and top plates where pipes are within 1 1/4 inches of the edge of the framing member
8 | 02 | Water Supply | Air test has 50 PSI minimum for 15 minutes; air tests may be required by the local administrative authority to be 80 PSI or more for 15 minutes (check local requirements)
9 | 02 | Water Supply | Water test has street pressure for 15 minutes
10 | 02 | Water Supply | No lead- or acid-bearing solders or fluxes used for potable water systems
11 | 02 | Water Supply | All cuts fully reamed
12 | 02 | Water Supply | Type M copper or galvanized pipe not used under slabs
13 | 02 | Water Supply | Soft copper tubing used underground
14 | 02 | Water Supply | Copper pipes supported every 6 feet
15 | 02 | Water Supply | Straps and hangers made of copper, copper plate, or plastic
16 | 02 | Water Supply | Main building water shutoff valve is a full-way valve
17 | 02 | Water Supply | Pressure reducing valves installed when the pressure at the meter exceeds 80 psi
18 | 02 | Water Supply | Temperature and pressure (T&P) relief valves and drains installed on water heaters
19 | 02 | Water Supply | Drains provided for pressure relief valves
20 | 02 | Water Supply | All hose bibs, valves, and pipe stub-outs to fixtures supported and secured
21 | 02 | Water Supply | Copper pipes and galvanized heating ducts have non-metallic separation
22 | 02 | Water Supply | Nail plates installed at studs, sole plates, and top plates where pipes are within 1 1/4 inches of the edge of the framing member
23 | 02 | Water Supply | Hose bibs (sill cocks) freeze-protected where installed in colder climates
24 | 03 | Plastic Pipe System | PEX (plastic) pipe supported every 4 feet
25 | 03 | Plastic Pipe System | No metal straps used with plastic pipe
26 | 03 | Plastic Pipe System | Minimum bend radius 12 times the nominal diameter of the tubing
27 | 03 | Plastic Pipe System | No plastic finish nipples or stub-outs
28 | 03 | Plastic Pipe System | Hose bibs secured so that torque on handles does not transmit to the plastic piping
29 | 04 | Drainage/Waste/Vent | Drainage and waste pipes have a uniform slope of 1/4 inch per foot
30 | 04 | Drainage/Waste/Vent | Vent pipes have a minimum slope of 1/4 inch per foot
31 | 04 | Drainage/Waste/Vent | Air test has 5 psi minimum for 15 minutes
32 | 04 | Drainage/Waste/Vent | Water test has 10 foot head (5PSI) of water for 15 minutes
33 | 04 | Drainage/Waste/Vent | All fixtures properly vented
34 | 04 | Drainage/Waste/Vent | Fixtures set level, in alignment with adjacent walls, and with proper clearances
35 | 04 | Drainage/Waste/Vent | Depth of shower dams and thresholds not less than 2 inches nor more than 9 inches
36 | 04 | Drainage/Waste/Vent | Finished floor of shower receptor has a uniform slope from the sides toward the drain of between 1/4 inch per foor and 1/2 inch per foot
37 | 04 | Drainage/Waste/Vent | Showers have door openings for minimum 22 inch door
38 | 04 | Drainage/Waste/Vent | Shower compartments greater than 1024 square inches and capable of encompassing a 30 inch circle
39 | 04 | Drainage/Waste/Vent | Trap vent at least two trap arm pipe diameters away from the trap weir
40 | 04 | Drainage/Waste/Vent | Cleanouts accessible at the final inspection
41 | 04 | Drainage/Waste/Vent | Cleanouts installed at the base of all stacks
42 | 04 | Drainage/Waste/Vent | Change of direction on horizontal piping between cleanouts does not exceed 135 degrees
43 | 04 | Drainage/Waste/Vent | Underground DWV not less than 2 inches
44 | 04 | Drainage/Waste/Vent | Water closets have 3 inch drainage pipes at least 2 inch vent pipes
45 | 04 | Drainage/Waste/Vent | Maximum of three water closets on 3-inch horizontal branch drains
46 | 04 | Drainage/Waste/Vent | Closet flanges secured to the floor with a fastener in each hole
47 | 04 | Drainage/Waste/Vent | No S-traps
48 | 04 | Drainage/Waste/Vent | No horizontal wet venting
49 | 04 | Drainage/Waste/Vent | No wet venting across floors or between stories
50 | 04 | Drainage/Waste/Vent | Vents connected to horizontal drains are taken off above the center line of the drain served
51 | 04 | Drainage/Waste/Vent | Condensate drains are provided near high efficiency furnaces, air conditioners, and heat pumps